PRODUCT DATASHEET GSP9-C40PV 600V DC 1000V DC Surge protective device

Application

This DC surge protective device is applied low voltage standard IEC/EN 61643-11 to protect against DC power line system and other equipment from over voltage and instantaneous over voltage damage. Widely used in photovoltaic comber box, power inverter, DC distribution cabinet etc. It has advantages of large discharge current, fast respond time, low residual voltage. Max. PV voltage up to UCPV ≤1000V dc.

Main features

1. High discharge capacity, quick response, plugged module.

2. Fast response time, din rail installation.

3. Double thermal disconnection devices, provide more reliable protection.

4. Green window means normal, red means defect, need to change module.

5. Remote signaling contact optional.

6. T1+T2 surge protection.

Technical parameter

| Model | GSP9-C40PV |  |
| --- | --- | --- |
| Test standard | IEC/EN 61643-11;GB18802.11 |  |
| SPD type | T1+T2/Class I+ II |  |
| Max. PV voltage [ Uc pv ] | 600V DC | 1000V DC |
| Nominal discharge current (8/20µs) | 20kA |  |
| Maximum discharge current(8/20µs) | 40kA |  |
| Iimp current (10/350µs) | 6.25kA |  |
| Poles | 2P | 2P/3P |
| Voltage protection level Up pv | 2.6kV | 3.6kV |
| Response time Ta | 25ns |  |
| Connection wire specification | 4mm2(L/N); 6mm2(PE) |  |
| Mounting | 35mm Din Rail |  |
| Matched fuse or circuit breaker | 32A |  |
| Type of remote signaling contact (Optional) | C+NC: Normally closed |  |
|  | C+NO: Normally open |  |
|  | C: Common contact |  |
| Max. Voltage/Current for remote signaling | 1A/2A/3A 125V AC |  |
| Wiring for remote signaling | 1.5mm2 max. |  |
| Operating temperature | -40°C to +80°C |  |
| Shell material | UL94-V0 fireproof material |  |

Dimension details (unit: mm)

Installation Diagram(2P&3P)