PRODUCT DATASHEET GSP9-C40PV 600V DC 1000V DC Surge protective device
Application
This DC surge protective device is applied low voltage standard IEC/EN 61643-11 to protect against DC power line system and other equipment from over voltage and instantaneous over voltage damage. Widely used in photovoltaic comber box, power inverter, DC distribution cabinet etc. It has advantages of large discharge current, fast respond time, low residual voltage. Max. PV voltage up to UCPV ≤1000V dc.

Main features
1. High discharge capacity, quick response, plugged module.
2. Fast response time, din rail installation.
3. Double thermal disconnection devices, provide more reliable protection.
4. Green window means normal, red means defect, need to change module.
5. Remote signaling contact optional.
6. T1+T2 surge protection.

Technical parameter
	Model
	GSP9-C40PV

	Test standard
	 IEC/EN 61643-11;GB18802.11

	SPD type
	T1+T2/Class I+ II

	Max. PV voltage [ Uc pv ]
	600V DC
	1000V DC

	Nominal discharge current (8/20µs)
	20kA

	Maximum discharge current(8/20µs)
	40kA

	Iimp current (10/350µs)
	6.25kA

	Poles
	2P
	2P/3P

	Voltage protection level Up pv
	2.6kV
	3.6kV

	Response time Ta
	25ns

	Connection wire specification
	4mm2(L/N); 6mm2(PE)

	Mounting
	35mm Din Rail

	Matched fuse or circuit breaker
	[bookmark: RANGE!B13]32A

	Type of remote signaling contact
(Optional)
	C+NC: Normally closed

	
	C+NO: Normally open

	
	C: Common contact

	Max. Voltage/Current for remote signaling
	1A/2A/3A 125V AC

	Wiring for remote signaling
	1.5mm2 max.

	Operating temperature 
	-40°C to +80°C

	Shell material
	UL94-V0 fireproof material



[bookmark: _GoBack][image: 3P 直流尺寸图]Dimension details (unit: mm)
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Installation Diagram(2P&3P)
[image: 3P 直流 接线图][image: 2P 直流 接线图]
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